|  | CFAS Enterprises Inc. After Market Utility Power Equipment Brokerage Mailto:Staff@CFASPower.com Turbine URL: http://CFASPower.com/Index.html Reciprocating URL: http://CFASPower.com/Recips.html |
| --- | --- |
| GTG_1301SC_EGT6551CC_50Hz.doc |  |

1 x 1998 EGT 6551B  37Mw 10500 V/3/50Hz 3000 Rpm

ON

1 X Harbin 15MW STG- Combined Cycle Power Plant

Price:  			USD $10MM Complete Plant

USD $7.35MM GT/Gen Only with Simple Cycle BOP

General Information:

YOM:					1998

CTG Hours:				8031.4, 748 Firing Times

ST-G  Hours:				5720.7,

Operation Times:			426

May 2006:				Medium Overhaul, Minor Repair, 300 Hours 							Since Repair

Fuel:					Diesel

Regular Borescope Inspections

Maintenance Implemented Yearly

Gas Turbine:				37 Mw EGT Model 6551B

Compressor:

17 Stages

11.8 Ratio

500x1000kg/H Flow

Turbine:				Axial

3 Stage

Inlet Temperature :			1104 Deg. C

Exhaust Temperature 		542 Deg. C

Starter: Diesel Engine

460Kw Detroit Diesel

12v-71

2 Stroke

Hydraulic Torque Coupling

Model E7WAT

1 Stage Pumping

Auxiliary Gearbox:			Model Aa51da

Multi-Shaft Driving

Forward Diesel Fuel Unit:		Rotring Engineering

Cooling Station:			Water Closed Cycling

Model:					BRBO 50

Cooling Area:				60m2

Water Purging Station:		Re-Clean Hpi 961

Rotring Engineering

Co2 Fire Extinguish Station:		Rotring Engineering

Load Gearbox:			Flender-Graffenstaden Model Trl 65cv

Electric Section -

Generator:				T60C

45.647 Mva

Voltage:				10500 V

Phase:					3

Frequency:				50 Hz

Amps:					2510

Insulation Grade 			F

Circuit Breaker:			Model VA8031/12/2PMA275

Vacuum Breaker

Auxiliary Transformer			400 Kva AEG

Exciter:				Model Tkj70/10

Brushless				5 Phases

200 Hz

252 Volts

522 Amps Dc

132 Kw

Exciter Transformer:			10.5kv/2*160 V

Dry Type

Gas Turbine Control Panel:		Mark V

3-Redundant Micro-Processor Control

Generator Protection And Exciter Adjustment

Integrated Circuit Model

DC System:				2 X Recharger Units

H3300

92 Ni-Cr Batteries Model SCM211

Capacity:				211AH

Steam Turbine/Generator Unit Mechanical Section -

Steam Turbine:			Harbin Steam Turbine Model N15-3.6/445

Rating:					15 Mw

Speed:					3000 Rpm

445 Deg. C Inlet Temperature

3.6 Mpa Inlet Steam Pressure

66 Ton/Hour Rated Steam Flow

High Pressure Oil Pump:		1 X Model 150AYII150*2B

Electric Motor: 			YB355S3-2

Rating:					220 Kw

Circling Water Pump:			3 X 600l-25a

Electric Motor:			 	Yl355-6

200 Kw

Auxiliary Circling Water Pump:	2 X 300l-35a

Electric Motor:				 Y280s-4

75 Kw

Closure Circling Water Pump:	2 X 8sh-13

Electric Motor:				250m-2

55 Kw

Condenser:				Semi-Half, Two Conduits, Surface Style

5 Ton/Hour

3 X Model 4n6x2 Condensing Pumps

Electric Motor:				Y2000l2-2

55 Kw

Circling Water Vacuum Pump:	2 X 2be12030

Electric Motor:			 	Y250m-6

37 Kw

Cooling Tower:			 Lianfeng Group FBL(II)-1500X3

Fan Model:				LF-60II

Electric Motor:				YDT280S-4/6

3 Units

Main Steam Gate:			Harbin Steam Turbine Model T104.301z

Automatic Close Device Model:	T104.302z

Electrical Section -

Generator:

Nanjing Steam Turbine Group 	Model Qfw-15-1-10.5

15 Mw

10500 V/3/50 Hz

Insulation:				F/B

AC Brushless Exciter:			Nanjing Steam Turbine Group Model Tflw70-3000

235 Volt

297 Amps

Everlast Magnetic Electricity Generator Model TFY2.85-3000C

Exciter Adjustment 			MAVR

HRSG:					Model Q393-542-66-3.82/450

Horizontal Arrangement, Single Pressure, Self-						Deoxygen, Self-Circling

3.82+/-0.05 MPA

450+/-5 Deg. C

66 Ton/Hour, Maximum Steam 66.7 T/H

Steam Drum Working Pressure :	4.22mpa

Gas Turbine Exhaust Air Specifications (Under Iso Condition);

511 T/H

542 Deg. C

Water Feed Pump:			Model Ft85-540

220 Kw

Gas Turbine Exhaust Gate:

Hangzhou Boiler Co. Model YD10.89

Hydraulic Station HGT007-32-01

Axial Fan Hangzhou Wuxing Fan Factory Model C9-19/5A, 11 Kw

Auxiliary Boiler:

2 X Shs25-3.82/445-Y, Steam Generation - 25 T/H

3 X Water Feed Pumps Dg36-50x10, 110 Kw

2 X Y4-73.12d, 90 Kw Fans

2 X 9-26 12.5d, 75 Kw Fans

Electric Equipment -

Changzhou Group Transformers:

#1 Main Transformer Model Sf8-50000/110 Kv

#2 Main Transformer Model Sf9-20000/110 Kv

#2 Plant Transformer Model Sc-1600/10

#3 Plant Transformer Model Sc-1000/10

#0 Plant Transformer Model Sc-1600/10

Breaker:				4 X Pinggau Sf6 Breaker Model Lw6a-110ii

7 X Chaozhou Senyuan Electrics KYN1B:10 						Manual Operated Vacuum Switch

110 Kv Current Mutual Indicator:

4 X Groups Hunan Heng Yang Mutual Inductor 						Model LCWB6-110W2

110 Kv Generatrix Voltage Mutual Inductor:

Jiangsu Rubu High Voltage Electrics JDW-							110w

Ups:					MGE P, 30 Kva

Controllable Silicon Current Adjustment Device:

Zuji Electrics Model Kcva-20

Re-Chargeable Group:		104 X 2v420ah Dry Fit

Transformer Protection:		3 X Xuji Electrics Pbh-113

Generator Protection:			Xuji Electrics Pfb-100

Line Protection:			2 X Nanrui Relay Protection Model Lfp-941b

Generatrix Protection:			Xuji Electrics Dcd-9

Electric Automation:			Xuji Electrics Xwjk-3000

Main Control System Devices -

Dcs System:				ABB Freelance 2000

DEH System:				Woodward 505e

Steam Turbine Monitoring And Protection System:

Bently Model 3300

Harbin Tuobin Automation Co. Model SG 8000

Water Treatment Control System:	GE Fanuc Model GE90-30PLC

Water Treatment System -

Pre-Treatment System:		De-Salt System

De-Salt Water Recovering System

De-Salt Water Ammonia Adding System

Inside Boiler Phosphate System

Water Adding System For Chemical System

Steam/Water Sample System

Fuel Discharge System

Diesel Fuel Treatment System:	Westfalia Model OSB35-02-066/40