|  | CFAS Enterprises Inc. After Market Utility Power Equipment Brokerage Mailto:Staff@CFASPower.com Turbine URL: http://CFASPower.com/Index.html Reciprocating URL: http://CFASPower.com/Recips.html |
| --- | --- |
| GTG_1478_Fm6CoGen50Hz.doc |  |

Unit No. 2  (CT) / 3 (ST-G)  - 1 x Used 53Mw Combined Cycle Plant Compiling of:

1 x John Brown PG6531B Gas Turbines on 1 x 16630KW Siemens ST-G

Asking Price: US  $6.355 MM (Fee Inclusive)

BOP Included

Spares for combined cycle.

#### Shenzhen City, No. A Combined Cycle Fm 6B  Power Plant

The power plant was founded in February of 1991 confirmed by the Ministry of Trade and Economy and the government of Shenzhen City. It is one of main gas turbine power plants of Shenzhen and it takes on chief power supply task for Shenzhen City. No.A power plant has two sets of 6B gas turbine and the supporting gas-steam combined cycle unit composed of waste heat boiler and turbo-generator.

No. 2 unit is PG 6531 gas turbine completely introduced from England John. Brown Engineering Limited. Company and manufactured by America GE Company. It was commercially run in December of 2000.

The turbine type of No. 2 gas turbine is single shaft and axial flow with 3 grades. The cylinder is horizontal mid-separate surface and it is cooled by the air. The compressor is IGV continuously adjusted and axial flow type and its pressure ratio is 11:7. The inlet is air filter device. The combustor of the gas turbine is adverse current can type and there are 10 combustors. The gas turbine is ignited through exited high pressure electrode type spark plug and there are 2 igniters. The flame detector is ultraviolet photoconductive and there are 4 flame detectors.

No. 2 gas turbine is started by electrical motor and the starting motor is C 315L57/2D from BRUSH Company. The power is 378 KW, the rotational speed is 2982 rpm and the power is 6.3 KV and 50 Hz.

Main Performance and Parameter of No. 2 Gas Turbines:

| No. | No. 2 Gas Turbine |
| --- | --- |
| Model | PG6531B |
| Manufacturer | England JBE |
| Ex-factory Serial Number | GT5114 |
| Rating | 36.5Mw |
| Total Running Hours | 55843 Hrs |
| Circulation Type | Combined circulation |
| Main Shaft Direction | Counterclockwise |
| Rotational Speed of Shaft | 5100rpm |
| Fuel | Light diesel oil |
| Control Mode | MK-IV |
| Basic Protection | Over-speed, overheating, vibration |
| Starting Mode | Started by AC motor |
| Equipment of Cooling Machine | Hydraulic jigger device |
| Running Mode | Continuous running |
| Amortization | Inlet and outlet silencer |
| Running Mode of Cooling Water | Closed circulation |

No. 2  Gas Turbine Nameplate Data (Standard Status and Basic Load)

| No. | No. 2 Gas Turbine |
| --- | --- |
| Basic Output | 36500 KW |
| Inlet Temperature | 15 (590F) |
| Turbine Inlet Temperature | 1104 |
| Exhaust Temperature | 543 |
| Inlet Pressure Drop | 101.6mmH2O |
| Exhaust Pressure Drop | 63.5mmH2O |
| Heat Rate | 11630KJ/KW.H |
| Heat Consumption | 424.1×106KJ/H |
| Efficiency | 30.95% |
| Air Flow | 491×103Kg/H |

Main supporting equipments and technical specification (standard status)

Compressor

| No. | No. 2 gas turbine |
| --- | --- |
| Compression Grade | 17 |
| IGV Mode | Continuously adjusted |
| Type | Axial flow |
| Cylinder | Horizontal mid-separation surface, vertical mid-separation surface |
| Pressure Ratio | 11．7 |
| Inlet Temperature | 15 |
| Inlet Pressure | 1013 millibar |
| Rational Speed of Shaft | 5100 rotates/min |

Turbine

| No. | No. 2 gas turbine |
| --- | --- |
| Type | Single shaft and axial flow |
| Grade Number | 3 |
| Rotational Speed | 5100rpm |
| Cylinder | Horizontal mid-separation surface |
| Cooling | Air cooling |

Combustor

Type: 						Adverse current can typed combustor

Quantity: 					10

Array: 						As the center of axial line of the unit and arranged 							according to the circle with same distance

Number: 					Numbered for air current counterclockwise, 							No. 10 is at the upper position of 12 o’clock.

Igniter type: 					exited high pressure electrode type spark plug

Quantity of igniter: 				2

Position of igniter: 				Located in 1# and 10# combustors

Flame detector type:				Ultraviolet photoconductive typed flame detector

Quantity of flame detector: 			4

Position of flame detector: 			located in No. 2 , No. 3 , 7# and 8# combustors.

Parameter for supporting equipments

Starting device of the gas turbine

No. 2  gas turbine starting motor 88CR

Model:					C315L57/2D

Manufacturer:				BRUSH

Power:					378KW(500HP)

Rotational speed:				2982rpm

Power:					6.3KV, 3Ph, 50hz

Hydraulic:				ratcheting pump

Model:				Gear pump

Rotational speed:			1725rpm

Working pressure;			94.90Kg/cm2

Capacity:				5.7L/min

Drive DC motor:			88HR (115VDC, 0.56KW)

Assistant gearbox

Model:					A519-B41

Function	a.	Directly connected with the rotor of the gas turbine;

b.	Connected or disconnected with the starting device;

c.	Drive the accessory of the gas turbine with corresponding rotational speed.

Rotational speed:	a.	Coupling of gas turbine: 5100rpm

b.	Main lubricating oil pump: 1415rpm

c.	Main hydraulic pressure pump: 1415rpm

d.	Atomization air compressor: 6000/45561rpm

Load gearbox

Type:						5-644B

Speed ratio: 					5100/3000

Rated power: 					42900KW

Lubricating oil system:

Main lubricating oil pump:

| No. | No. 2 gas turbine |
| --- | --- |
| Model | Gear box |
| Rotational Speed | 1415rpm |
| Volume | 1741C/MCM |
| Outlet Pressure | 4.56Kg/cm2 |
| Drive | Assistant gearbox |
| Manufacturer | JBE |

AC assistant lubricating oil pump

| No. | No. 2 gas turbine |
| --- | --- |
| Type | Centrifugal |
| Flow | 1714L/MCN |
| Working Pressure | 4.48 |
| Rotational Speed | 2950rpm |
| Drive | Three-phase motor 88QA(30KW) |
| Manufacturer | JBE |

DC emergency lubricating oil pump

| No. | No. 2 gas turbine |
| --- | --- |
| Type | Centrifugal |
| Flow | 946L/min |
| Working Pressure | 2Kg/cm2 |
| Rotational Speed | 1500rpm |
| Drive |  |

Lubricating oil box

Full oil level: 305 mm from top

Volume for full oil level: 6433 liter

Low oil level: 4006 mm from top

High oil level alarm 254mm

Low oil level alarm 432mm

Lubricating oil cooler

Type: horizontal shell “U” pipe-typed heat exchanger (water is through the inner pipe while oil is through the outer pipe)

Quantity: 1 for cross loop line layout, one working while one standby.

Normal outlet oil temperature: 54.4+1.7?

Main lubricating oil filtration

Type F3-9XE Filtration precision: 5μ

Quantity 1 (cross loop line layout, exchangeable, one working while one standby)

Maximum working pressure: 8.44 Kg/cm2

Maximum permissible inlet and outlet pressure difference: 1.2 Kg/cm2

Lubricating oil heater (23QT-1,-2)

Type: immersion type heater

Quantity: 1

Parameter: 15 KW 380V, 3-phase, 50HZ, 10.43A

Control oil filtration

Type HP-511-125-1-1

Filtration precision: 5μ

Quantity: 1 (cross loop line layout, exchangeable)

Maximum working pressure: 8.78Kg/cm2

Maximum permissible inlet and outlet pressure difference: 1.2Kg/cm2

Hydraulic oil system

Hydraulic oil pump (PH-1)

Type: piston pump

Rotational speed: 1415rpm

Working pressure: 94.90Kg/cm2

Flow: 68.4L/min

Drive: assistant gearbox

Hydraulic pressure filter (PH-1.2)

Type: single pipe type

Filtration precision: 0.5μ

Quantity: 1 (cross loop line layout, exchangeable)

Maximum permissible inlet and outlet pressure difference: 4.2Kg/cm2

Cooling water system

Cooling water system of No. 2  gas turbine

The cooling water system of No. 2  gas turbine is the closed circulation

With 7 sets of 11 KW cooling fans numbered 88FC-1, 2, 3 and FG-1, 2, 3, 4

CO2 fireproof system

No. 2  gas turbine:

CO2 automatic fire extinguishing system, used for the gas turbine and motor separately.

Gas turbine CO2  total volume 15 bottles

Motor CO2  total volume 5 bottles

Specified value of fire probe 316

Bottling pressure should be more than 800PSI

IV.	No. 2 Boiler

No. 3 boiler supporting with No. 2 gas turbine is the horizontal waste heat boiler produced by Holland Standard Fasel Company and NK50/70/0—3Da turbo-generator produced by Germany Siemens Company. The whole set of fuel-steam combined cycle unit was run in Nantian Power Plant in December of 1994.

Main Parameters of No. 2 Boiler:

| Equipment Name | Equipment Parameters |
| --- | --- |
| High pressure steam drum | Inner diameter 1530㎜, wall thickness 35㎜, material 20g, internally set steam and water separation device, such as cyclone separator |
| Low pressure steam drum | Inner diameter 1676㎜, wall thickness 12㎜, material 20g, internally set steam and water separation device, such as cyclone separator |
| Super-heater | 3 groups of curtain panel, 432 pipes, specification: 50.8*3, material: 15crmo and 8m long |
| High pressure evaporator | 9 groups of curtain panel, 1296 pipes, specification: 50.8*3, material: 20g and 8m long |
| Economizer | 8 groups of curtain panel, 1152 pipes, specification: 50.8*3, material: 20g and 8m long |
| Low pressure evaporator | 5 groups of curtain panel, 720 pipes, specification: 50.8*3, material: 20g and 8m long |
| Deaerator | Rated output: 88t/h, working temperature: 0.8bar, working temperature: 105, produced by Wuxi Boiler Factory |
| Soot blower | Pulse blasting type soot blower, produced by Harbin Modern Technology Co., Ltd. |
| Blowdown system | Type: DP-3.5, cubage: 3.5 m3, working pressure: 1.5BAR, produced by Wuxi Boiler Factory |
| Steel frame and wall plate of the boiler | I-beam, heat preservation thickness 150, inner guard plate is stainless steel plate |
| Transition flue duct | I-beam, heat preservation thickness 150, inner guard plate is stainless steel plate |
| Chimney | Diameter: Ф2000㎜, 25 m high and the steel plate is 14㎜ thick |

Parameters of Auxiliary Equipments

| No. | Equipment Name | Quantity | Equipment Parameters |
| --- | --- | --- | --- |
|  | High pressure feed water pump | 2 | Type: WKF/80/10, lift: 520M, flow: 75t/h, manufacturer: KSB (Italy) |
|  | Low pressure feed water pump | 2 | Type: G32-250.1, lift: 70M, flow: 17t/h, manufacturer: KSB (Italy) |
|  | Dosing device | 4 | Type: KW282-18A 11SA1, manufacturer: ALLDOS (Germany) |

V.	No. 3 Turbine

No. 3 turbine mainly includes turbine body, condenser system, circulation cooling water system, lubricating oil system, hydraulic oil system, jigger system, rubber ball cleaning system, control oil system and oil cooler.

Main parameters of ＃3 turbine:

Turbine body

Manufacturer: 						Germany SIEMENS

Model:							NK50/71/0-3DA

Type: 							single cylinder, single current, 									reverse, pumping and condensing 									turbine

Delivery date:						 December of 1994

Rated output of motor: 					16880KW

Entrance steam pressure of auto main stop valve: 	39.79 kg/cm²A

Entrance steam temp of automatic main stop valve: 	445

Rated steam flow: 					66T/N

Exhaust pressure: 					0.087kg/cm²

Rated rotational speed of turbine: 			6300rpm

Rated rotational speed of turbine motor: 		1500rpm

Turning direction of turbine motor: 			left (from turbine to motor)

Connection of turbine and motor: 			speed change gear box

Entrance temperature of cooling water: 			20~30

Flow of cooling water: 					3487-3600m³/H

Jigger

Type:							 AC motor drive hydraulic jigger

Rotational speed: 					150 rpm

Oil system design parameters

Type of lubricating oil: 					TD46 turbine oil

Flow of lubricating oil:

Radial bearing before turbine: 				3.1 m³/HR

Radial bearing after turbine: 				7.0 m³/HR

Turbine thrust bearing: 					6.0 m³/HR

Gear box: 						42.4 m³/HR

Opposite wheel: 						1.2 m³/HR

Motor: 							1.8 m³/HR

Security system: 						2.0 m³/HR

Control oil: 						6.6 m³/HR

Dynamic oil: 						46.7 m³/HR

Total oil: 							(excluding dynamic oil) 70.0m³/HR

Oil system pressure:

Normal running lubricating oil pressure: 		1.7- 2 kg/cm²

Normal running lubricating oil temperature: 		45±3

Control oil pressure: 					9 kg/cm²G

Tripping oil pressure: 					8 kg/cm²G

Jigger oil pressure: 					6 kg/cm²G (zero rotational speed)

1.5- 2 kg/cm²G (normal jigger)

Axis culmination oil pressure: 				117.2 kg/cm²G

Lubricating oil box:

Normal volume:						10M³

1st filling oil 11M³

Highest oil level: 						(measured from the top) 460mm

Lowest oil level: 						(measured from the top) 560mm

Steam pressure and temperature:

Main steam pressure:					 (design) 39.79 kg/cm²

Normal running pressure: 				39.79 kg/cm²

Permissible pressure: 					43.87 kg/cm² (forbid exceeding for norm 									running)

Permissible pressure: 					47.95 kg/cm² (12 hours of each month max)

1st grade of impeller room pressure 35 kg/cm² 1st grade of nozzle and 1st grade of guided vane)

Main steam temperature: 				445℃

Normal running temperature: 				445℃

Permissible temperature: 				453℃ (forbid exceeding for normal running)

Permissible temperature: 				459℃ (400 hours of each month max)

Permissible temperature: 				473℃ (80 hours of each month max)

Min starting time for cold status starting: 		20min

Min load time for cold status starting: 			73min

Min full load time for cold status starting: 		93min

Turbine control and safety device

Turbine control

Type: TS310 electro-hydraulic controller

Adjustment system: 					speed governing steam door 									and nozzle adjustment

Speed governing scope: 					no load speed governing scope 									+7﹪-15﹪ rated rotational speed

TS310 over-speed tripping system

Type: 							electrical over-speed tripping system

Tripping speed: 						110﹪±1﹪ rated rotational speed

Technical parameters for main auxiliary devices:

Main oil pump						one set

Type: 							centrifugal

Outlet pressure: 						9 kg/cm²

Rated volume: 						80 m³/HR

Drive mode: 						main shaft drive of turbine

Manufacturer: 						SIEMENS

Ex-factory date: 						1987

Delivery date: 						December of 1994

AC auxiliary oil pump

Type: 							Centrifugal

Outlet pressure: 						8.26kg/cm² (normal running);

6 kg/cm² (hydraulic jigger)

Rated volume: 						72 m³/HR (normal running);

132m³/HR (hydraulic jigger)

Rotational speed: 					2950 rpm

Drive motor: 						55kw, 2960 rpm

Manufacturer: 						HALBERG

Delivery date: 						October of 1994

Accident DC oil pump:					 one set

Type: 							Centrifugal

Outlet pressure: 						1.8kg/cm²

Rated volume: 						51 m³/HR

Rotational speed:					 2900 rpm

Drive motor: 						5.7kw，2960 rpm

Manufacturer: 						HALBERG

No.: 							NOPZ: 50/13

Delivery date: 						October of 1994

Axis culmination oil pump				one set

Model: 							CB-FA18-FL

Type: 							gear type

Outlet pressure: 						140kg/cm²

Rated volume: 						18 ml/rotate

Rotational speed: 					1800 rpm

Manufacturer: 						Shandong Yuci Hydraulic Part Factory

Delivery date: 						October of 2004

Condenser							one set

Type: 							single flow

Tube quantity: 						2400

Tube diameter: 						Dn17mm

Tube length: 						5.460M

Tube material: 			 			Cu Zn 28	Sn F38

Normal flow of circulating water: 			969KG/S

Max flow of circulating water: 				1070KG/S

Pressure loss of circulating water: 			207mbar (normal flow)

Inlet and outlet pipe diameter of circulating water: 	Dn700mm

Ex-factory date: 						December of 1987

Delivery date: 						October of 2004

Vacuum pump						two sets

Model: 							2BE1203-OFY4

Max power: 						29 kw

Rotational speed:					980 rpm

Flow of seal water:					6.5 m³/H

Drive motor: 						1LA6253-6AAD 380V/50HZ

Motor power: 						37 kw

Rotational speed of motor: 				980 rpm

Manufacturer: 						SIEMENS

Ex-factory date: 						1988-year

Delivery date: 						1994-10

Rubber ball cleaning pump				one set

Model: 							ROWA-B-65.20-2NL-P

Flow: 							60 m³/H

No.: 							47852

Power: 							31.3 kw

Rotational speed: 					1450 rpm

Lift: 							13M

Ex-factory date: 						April of 1988

Delivery date: 						October of 1994

Condensing water pump					two sets

Model: 							CBSY10040，B521.0E

Flow: 							70.25 m³/H

No.: 							P-C190175/190185

Power: 							17.6 kw

Rotational speed: 					1450 rpm

Lift: 							50M

Inlet temperature: 					42.5℃

Drive motor: 						22 kw, 380V, 50HZ, 40A, 1465 rpm

Manufacturer: 						HALBERG

Ex-factory date: 						April of 1988

Delivery date: 						October of 1994

Circulation water pump: 					two sets

Model: 							Centrifugal

Model: 							24SH-19

Flow: 							3168 m³/H

Lift: 							32 M

Permissible absorbed vacuum: 				2.5M

Shaft power: 						310 kw

Rotational speed: 					970 rpm

Efficiency: 						89％

Weight: 							2220KG

Ex-factory date: 						March of 1988

Manufacturer: 						Shenyang Water Pump Factory

Drive motor: 						380 kw, 6KV, 50HZ, 44A, 990 rpm

Delivery date: 						October of 1994

Lubricating oil box exhaust fan				one set

Type: 							M66-2

Power: 							0.28 kw

Ex-factory date: 						March of 1988

Delivery date: 						October of 1994

Circulated water cooling tower fan			three sets

Model: 							LF-77A

Rotational speed: 						149rpm

Wind: 							135 m³/H

Vane quantity:						4

Fan efficiency: 						83.8﹪

Fan power: 						57 kw

Drive motor: 						75 kw, 380V, 139.6A, 50HZ

Delivery date: 						October of 1994

VI.	Technical Parameters of Electric Equipments

1.	Technical Parameters of Motor:

| No. | No. 2 | No. 3 |
| --- | --- | --- |
| Type | Gas turbine motor | Steam turbine motor |
| Code | GTG2 | STG3 |
| Manufacturer | BRUSH | BRUSH |
| Model | BSGMD | BSGMD13126/4 |
| Standard | IEC34-1 | IEC34-07 |
| No. | 36167A-4G | 36169A-1G |
| Ex-factory Date | 1987.8 | 1987.8 |
| Delivery Date | 1990.3 | 1994.12 |
| Output Volume | 43741KVA | 20820KVA |
| Rated Power | 36700KW | 16630KW |
| Stator Voltage | 10500V | 10500V |
| Stator Current | 2405A | 1145A |
| Phase Number | 3 | 3 |
| Frequency Current | 50HZ | 50HZ |
| Rotational Speed | 3000rpm | 1500rpm |
| Short Circuit Ratio |  |  |
| Power Factor | 0.85 | 0.85 |
| Excitation Voltage | 158v | 89A |
| Excitation Current | 937A | 307A |
| Stator DC Resistance | 0.010025 | 0.003955 |
| Rotor DC Resistance | 0.0126 | 0.156 |
| Stator Insulation | F | F |
| Rotor Insulation | F | F |

2.	Technical Parameters of Main Exciter:

| No. | No.２ | No.３ |
| --- | --- | --- |
| Model |  | XL79.14/20 |
| Volume | 178KW | 60KW |
| Output Voltage (Empty/ Full) | 31/173V | 26/115V |
| Output Current (Empty/ Full) | 263/1030A | 170/525A |
| Excitation Pressure | 45V | 48.8V |
| Excitation Current | 6.1A | 6.2A |
| Armature, Magnetic Field Insulation Grade | F | F |

3.	Technical Parameters of Auxiliary Exciter:

| No. | No.２ | No.３ |
| --- | --- | --- |
| Model | BMX-34-10 | BMX-34-10 |
| Excitation Mode | Permanent magnet | Permanent magnet |
| Volume | 3KVA | 1.57KVA |
| Frequency | 400HZ | 250HZ |
| Output Current | 15A | 5.8A |
| Output Voltage | 200V | 270V |
| Insulation Grade | F | F |

4.	Motor Air Cooler:

| No. | No.２ | No.３ |
| --- | --- | --- |
| Cooling Mode | Air cooling | Air cooling |
| Ventilation Model | Opened circulation | Opened circulation |
| Flow of Cooling Water |  |  |

5.	Motor Neutral Point Grounding Equipment:

| No. | No.２ | No.３ |
| --- | --- | --- |
| Grounding Mode | Arrester grounding | 13.8KV/240V grounding transformer |
| Grounding Resistor |  | 0.25 |

6.	Technical Parameters of Motor Outlet Circuit Breaker:

| No. | 52G | 53G/52AU |
| --- | --- | --- |
| Model | VRBSG-12/3050 | VRBSG-12/1250 |
| Rated Pressure | 12KV | 12KV |
| Rated Current | 3150A | 1250A |
| Blockage Current | 50KA | 50KA |
| Operation Institution | Spring energy accumulation | Spring energy accumulation |
| Operation Mode | Manual and electrical | Manual and electrical |
| Control Pressure | 110VDC | 110VDC |
| Manufacturer | ＡＳＣＥ (Italy) | ＡＳＣＥ(Italy) |
| Ex-factory Number | LHO17212 |  |
| Note: | Ex-factory number for 52AU is LHO7215 |  |

7.	Technical Parameters of Main Transformer:

| No. | No.２ | No.３ |
| --- | --- | --- |
| Model | SF7-50000/110 | # SF7-20000/110 |
| Rated Volume | 50MVA | 20MVA |
| Rated Pressure |  |  |
| Rated Current | 238.6/2750A | 95.4/1099A |
| Phase-Number/ Frequency | 3/50 | 3/50 |
| Impedance Pressure | 9.67% | 10.5% |
| Coupling Mode | YO/D-11 | YO/D-11 |
| Cooling Condition | OFAN | ONAN/ONAF |
| No-load Current | 0.27% | 0.9% |
| No-load Consumption | 47.3KW | 27.5KW |
| Load Consumption | 218.8KW | 104KW |
| Insulation Level | LI480AC200 |  |
| Voltage Regulation Mode | No load voltage regulation | No load voltage regulation |
| Product Code | IET71013059 | IET710135019 |

8.	Technical Parameter of Transformer for Factory:

| No. | 61B | 40B/41B | 42B/43B |
| --- | --- | --- | --- |
| Model | SL7-3150/10 | BS7-800/10 | SL7-1250/6 |
| Rated Volume | 3150KVA | 800KVA | 1250KVA |
| Rated Pressure | 10.5/6.3KV | 10.5/0.4KV | 6.3/0.4KV |
| Rated Current | 175.6/288.7A | 43.90/1154.7A | 68.6/1804.2A |
| No-load Consumption | 3.65KW | 1.54KW | 2.20KW |
| Impedance Pressure | 5.5% | 4.5% | 4.51% |
| Coupling Mode | Y/D-11 | D/YO-11 | Y/YO-12 |
| Cooling Condition | ONAN | ONAN | ONAN |
| Voltage Regulation Mode | No load voltage regulation | No load voltage regulation | No load voltage regulation |
| Manufacturer | Shenyang Transformer Factory |  |  |

9.	110KV SF6 Circuit Breaker

| No. | 1101,1102,1103,1104,1220 |
| --- | --- |
| Model | LW6-110IW |
| Rated Pressure | 110KV |
| Rated Current | 3150A |
| Blockage Current | 31.5KA |
| Rated Operation Order | Closing-0.35—closing and separating－1805-- closing and separating |
| Rated SＦ６ air pressure | 0.6Mpa |
| ＳＦ６ Gas Weight | 14KG |
| Operation Institution | LW6-110IW hydraulic pressure institution |
| Operation Pressure of Closing Brake | 220DC |
| Operation Pressure of Separating Brake | 220DC |
| Motor Power | 220DC |
| Heater Power | 220AC |
| System Nitrogen Pressure | 1.8Mpa |
| Rated Operation Pressure | 32.6Mpa |
| Oil Pump Starting Pressure | 31.6Mpa |
| Oil Pump Stopping Pressure | 32.6Mpa |
| Manufacturer | Pingdingshan Switch Factory |

10.	10.5kv. 6.3kv Vacuum Switch Cabinet:

| No. | 51G | 52G | 53G | 611 | 614 | 621 |
| --- | --- | --- | --- | --- | --- | --- |
| Model | JYNC-10 | VRBSG-12 | VRBSG-12 | 3AF |  | 3TL6 |
| Rated Voltage | 10KV | 12KV | 12KV | 6.3KV | 6.3KV | 6.3KV |
| Rated Current | 3150A | 3150A | 1250A | 1250A | 630A | 400A |
| Blockage Current | 50KA | 50KA | 50KA | 25KA |  |  |
| Operation Institution | Energy storage type | Energy storage type | Energy storage type | Energy storage type | Energy storage type | Energy storage type |
| Operation Mode | Electrical/ manual | Electrical/ manual | Electrical/ manual | Electrical/ manual | Electrical/ manual | Electrical/ manual |
| Control Voltage | 110VDC | 110VDC | 110VDC | 110VDC | 110VDC | 110VDC |
| Manufacturer | Beijing Switch Factory | SACE | SACE | SIMENS | SIMENS | SIMENS |
| Note | 51AU is the same as 100，but its control voltage is 220 DC |  | Same as 52AU | Same as 610 | Same as 615 | Same as 622/623 /624/625/626 |

11.	Disconnector and Grounding Switch:

| Model | Rated Voltage | Rated Current | 4# Heat Stable Current | Permissible Connection Pull | Auxiliary Institution | Application Location |
| --- | --- | --- | --- | --- | --- | --- |
| GW4-110DW | 110 | 1250A | 31.5KA | 500N | CJ5 | 110KV system |
| GWB-60GW | 60KV | 400A |  |  |  | 1#,No. 3 main change neutral point |
| GWB-60GW | 60KV | 600A |  |  |  | No. 2 main change neutral point |

12.	Current Transformer:

| Model | Rated Voltage | Rated Current Ratio | Accurate Grade | Application Location |
| --- | --- | --- | --- | --- |
| LCWB6-110W | 110KV | 2*300/5 | 0.5/B/B/B | 1220/1101 |
| LCWB6-110 | 110KV | 2*300/5 | 0.5/B/B/B | 1102/1103 |
| LRB-60 | 60KV | 300/5 | 05.B | 1# main change neutral point |
| LCW2-35 | 35KV | 200/5 |  | No. 2 ,No. 3 main change neutral point |
| LZZBJ9-10 | 10KV | 3000/5 | B/B | 1# motor wiring out and branch for factory |
| LMZ1-10 | 10KV | 3000/5 | 0.5/B/B/B | 1# motor neutral point |
|  | 10KV | 3000/5 | 0.2/5P20/X/X | No. 2 motor neutral point |
|  | 10KV | 3000/5 | 0.5/5P20 | No. 2 motor wiring out and branch for factory |
|  | 10KV | 1200/5 | 0.2/5P20/X/X | No. 3 motor neutral point |
|  | 10KV | 1200/5 | 0.5/5P20 | No. 3 motor wiring out |
| JZZBJa-10A | 10KV | 100/5 | 0.5/B | 10kv |

13.	Voltage Transformer:

| Model | Type | Phase No | Voltage Change Ratio | Accurate Grade | Volume | Application Location |
| --- | --- | --- | --- | --- | --- | --- |
| TYD | Outdoors type | 1- phase |  | 1/3P | 300VA | MeimeiＩ wiring out |
| JCC6-110W | Outdoors type | 3-phase |  | 1/0.5/3P | 300VA | 110kv bus |
| JDZJ-10 | Outdoors type | 3-phase |  |  |  | 1# motor and 100 switch wiring in |

VII.	Control System

The control systems of PG6531 gas turbine in the power plant are MARK control systems. The hardware configuration and control function for these 2 sets of control systems are basically same as follows:

MARK control system is made as central configuration of 16-bit Intel 8086 microprocessor. The main control function is through triplex hot-redundancy microprocessor and three independent processors are completely same. After the logic control command from three controllers has been voted 2/3, the analog control command of three controllers is piled and averaged in three-loop electro-hydraulic server valve. During running, if any one controller fails, the other two controllers go on controlling the gas turbine. After the failed controller has been repaired, it can work again and it doesn’t influence the gas turbine’s running.

Hardware configuration of control system:

There are four system hardware, <R>, <S>, <T> and <C>. <R>, <S> and <T> are different controllers, which are composed of the same CPU and block modules to fulfill main control and protection function, so it is called <RST> controller. <C> is named as communication device. The three independent RS232 serial data connectors are connected through <C> and <R>, <S> and <T>.<RST> controller is composed of contact input module, analog input and output module, thermocouple/ thermal resistance input module, synchronization module, flame detector module, relay drive module and relay module as the core of <RST> module and it is connected with operation interface and communication device for key control, protection function, diagnosis test and communication device <C> data exchange of the turbine.

The communication device <C> is connected with one printer and one CRT for monitoring and printing running data and implementing non key control, protection and diagnosis test functions.

Control function：

Starting control

The turbine’s running is through common function of procedure system and starting control. After the operation selection switch on the operation interface delivers starting command, the procedure system examines preparation starting permissible condition, blocks closure resetting, starts auxiliary equipment and lets starter push the turbine to igniting rotational speed and igniting according to corresponding valve and motor of the procedure switch and judge whether it has successfully ignited and then it warms up or cleans and closes the starter until the turbine’s rotational speed turns to running speed and finishes starting procedure. From igniting to procedure completion, the starting is controlled by fuel.

Rotational speed control

MARK  control system has two control arithmetic, including droop control mode and zero-droop control mode. The system load control device has three pre-specified values, such as max load, pre-selected load and turning spared load to realize automatic load control.

Acceleration control

The acceleration control system only limits the acceleration at the dynamic course with increasing rotational speed, which has function in following matters: limit the acceleration rate of the turbine during starting to reduce heat strike of heat parts and help to restrict dynamic over-speed after the turbine accidentally throws the load.

Temperature control

The control system has temperature control system, which indirectly controls turbine inlet temperature through controlling exhaust temperature of the turbine. The exhaust temperature signal is average after being measured exhaust temperature by 18 thermocouples and eliminating trouble signal. The temperature control baseline is changed along with the environmental temperature change, and it has two modification modes, it is changed with the compressor’s outlet pressure or it is changed with the fuel baseline’s change. The former is main temperature control line and the latter is the standby temperature control line.

Synchronization control

The automatic synchronization control system measures voltage, power and phase position of motor and circuit, and it sends closing command for meeting the condition

Fuel control system

The turbine control system of the plant is liquid fuel control, including light oil-heavy oil exchange control function and it realizes fuel control through control refluence mode. The triplex hot-redundancy <RST> controller outputs control current and drives electro-hydraulic server valve three-loop and the rotational speed signal of the fuel distributor is fed back as fuel flow signal. The control system can be changed to gas fuel or liquid/ gas fuel system.

Control of compressor adjusting inlet guide vane

Turn down the inlet guide vane for part rotational speed to avoid compressor’s vibration; for part load, turn down the inlet guide vane to improve exhaust temperature and improve combined cycle efficiency. The triple hot-redundancy <RST> controller outputs control current and drives electro-hydraulic server valve three-loop and LVTD inspects adjustable guide vane’s opening degree.

MARK  protection system

When the gas turbine unit has trouble, the unit will be away from the normal running parameters, and then the protection system sends alarm and indicates trouble place so that the operators will be waken and they will eliminate trouble immediately and then the unit will be back to safe running status. If the gas turbine unit has larger trouble, MARK Ⅳ protection system alarms while it blocks the unit and protects it. The main protections are including:

Protection for low oil pressure of lubricating oil;

Protection for high temperature of lubricating oil;

Over-speed protection;

Superheating protection;

Flameout protection;

Burning trouble protection;

Machinery vibration high protection;

Control trouble protection.

After the 6B units have been delivered and run, the unit has reliable technology, stable performance and convenient starting and stopping. For burning with light diesel oil, the units fundamentally reach their rated output and the operation maintenance is dropped. Along with increasing international oil price, the power plant reconstructed two sets of 6B units for their heavy oil technology at the early of 2001, on June 10 of 2001 and August 15 of 2001, No. 2 turbine has been successfully burnt 180cst heavy oil to realize the great stride for the production technology of the power plant and then A power plant obviously improves its economic benefit.

6B unit has been burning 180cst heavy oil from 2002 to 2006, with relative technicians’ careful operation and maintenance, in recent 4 years, the unit has stable running, the equipments have better health status, the unit has normal starting and stopping and the power supply oil consumption rate always keeps about 114g/kw.h, additionally the units’ performance, efficiency and benefit are all in better level. At present, the 6B units has three fuel modes, namely, independent burning light oil, independent burning heavy oil. The light oil-heavy oil have very good adjustment performance with any proportion. For burning with heavy oil, all indexes of the smoke exhaust reach the environmental protection requirement, under the environmental protection requirement and strict control of Shenzhen, the 6B unit has been passed combined acceptance of Shenzhen Environmental Protection Bureau on September 16 of 2003 and the plant has got the qualified letter. During Shenzhen Environment Inspection Station inspects the smoke carbon dioxide, nitrogen oxide, soot and heavy oil treatment waste water of the 6B unit each year, all indexes completely reach the national control standard.

Additional: No. 2  turbine of the plant has been changed from oil to steam in September of 2006, after which, the unit has been run normally.

I.	Gas Turbine Specification

| Turbine No. | Turbine Model | Brand Output Thousand KW | Heat Consumption Kj/kwh | Exhaust Temperature℃ | Delivery Time | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
| No. 2 turbine | PG6531 | 3.65 | 11630 | 543 | 1994.12 | England JBE |

II.	Waste Heat Boiler Specification

| Boiler No. | Boiler Model | Rated Evaporation (t/h) | Rated Steam Pressure (bar) | Rated Steam Temperature (℃) | Delivery Time | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
| No. 2 boiler | - | 66 | 40 | 445 | 94.12 | Holland fasfl |

III.	Turbine Specification

| Turbine No. | Turbine Model | Brand Output Thousand KW | Rated Steam Pressure (bar) | Rated Temperature (℃) | Delivery Time | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
| ＃3 turbine | NK50/71/0--3Da | 1.688 | 39.79 | 445 | 94.12 | Germany Siemens |

IV.	Motor Specification:

| Motor No. | Model | Rated Volume (MW) | Stator Pressure (KV) | Cooling Medium | Delivery Date | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
| No. 2 motor | BSGMD | 3.67 | 10.5 | Air | 1990.3 | BRUSH |
| No. 3 motor | BSGMD131260/4 | 1.668 | 10.5 | Air | 1994.12 | BRUSH |

V.	110KV Main Transformer (No-load Voltage Regulation)

| No. | Model | Impedance Pressure % | Coupling Mode | Cooling Mode | Delivery Date | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
| No. 2 main transformer | SF7-50000/110 | 9.67 | YND11 | OFAN | 1988.8 | Shenyang Transformer |
| No. 3 main transformer | SF7-20000/110 | 10.5 | YND11 | ONAN ONAF | 1994.12 | Shenyang Transformer |